| Safe System of Work |  |
| --- | --- |

| Company name | Elite Services Holdings Ltd | Department | Service |
| --- | --- | --- | --- |

| Contract | Customers Site | Prepared By | Gareth Lewis |
| --- | --- | --- | --- |

| Date prepared | 01/05/2024 | Review date | 01/05/2025 |
| --- | --- | --- | --- |

1. DESCRIPTION OF WORK

The installation of Hand dryers, Ozone Generators, Air Sterile and Omniscient

2. PERSONNEL COMPETENCE REQUIRMENTS

The Personnel completing electrical installations is competent to do so and is fully trained in line with the latest City & Guilds BS7671 British Standards. The Personal is also trained as a domestic installers and deemed competent by the NICEIC standards agency A copy of our certificates of competence can be made available at the customers request

3. SUPERVISORS DUTIES AND RESPONSIBILITIES

Gareth Lewis will supervise and assess all electrical work that is to be carried out. Duties also inc: to ensure that all personnel involved in the installation process are fully trained and are carrying the correct PPE.

4. MEANS OF ACCESS

Access is required to all areas where equipment is located. Some wiring may need to be fitted behind panels, walls, voids and roof spaces. Step Ladders and Panel lifters are to be used where necessary.

5. MACHINERY, PLANT AND EQUIPMENT

Battery Operated Drill, Panel lifters, Assorted Cable, Assorted hand tools e.g.: screwdrivers & Wire cutters, Stud Detector, Voltage detector, Step Ladders, MCB Lock Out, Calibrated Multi-function Tester

6. LIFTING OPERATIONS AND EQUIPMENT

N/A

7. MATERIALS STORAGE, SECURITY AND HANDLING

N/A

8. INSTALLATION METHOD

Ensure the area is closed off and ‘2 meter’ social distancing rule is possible. Ask the customer if there is any asbestos on site, if so ask for a copy of the Risk Assessment and plan of any area containing Asbestos prior to drilling. You MUST NOT drill if there is any Asbestos in the vicinity of the install area. - Restrict access to the installation area. - With the customer, agree the position for where the equipment is to be fitted. - Drill and securely fasten the equipment to the wall using the appropriate fixings. - Using a flexible cable, connect up the equipment leaving an appropriate length to reach the fused spur. - If there is a fused spur readily available then this should be utilised. Isolate or lock off the spur by either removing the fuse or switching the MCB off and placing a lock on it. (Lock off Keys and fuses are strictly to be kept on the person carrying out the installation until completion. This is to stop the risk of accidentally livening up the system) - Check with a proven voltage tester that the spur has been isolated, if found to be safe then complete the wiring connection to the outgoing terminals of the spur. The following 4 operations are only applicable if there is not an adequate electrical supply - Install a fused spur adjacent to the equipment, drill and fix spur to the wall - Connect the wired flex from the equipment to the outgoing terminals of the spur. - Connect a cable to the incoming terminals of the spur and run it to the nearest adequate supply (this may be the distribution board) isolate the relevant circuit by switching off its MCB and placing a lock off tool onto it. - Check with a proven voltage tester that the circuit has been safely isolated before connecting the run cable to the relevant outgoing terminals. Inspection & Testing Before livening up the circuit inspect the circuit and complete the following tests: - R1&R2 Continuity - Insulation Resistance - Polarity - Adequacy of bonding (if applicable) Replace fuses/Remove MCB locks are energise the circuit and complete the following tests: - Voltage check - Maximum earth fault loop impedance - RCD operating time (if applicable) - Operation of equipment installed, adjust settings if required as per manufactures settings. On Completion of Installation - Complete an Installation/Minor works certificate - Clean and Tidy the working area - Replace any removed panels if applicable - Inform customer and show them how to work the equipment (if applicable) - Re open installation area - Remove gloves, wash/sanitize hands

9.PERSONAL PROTECTIVE EQUIPMENT

Safety Glasses, Safety Footwear, Safety Gloves, Safety Helmet, Ear Defenders, KN95 protective mask

10. PROTECTION OF THIRD PARTIES

Close of area, erect warnings signs, lockout on customers distribution board if applicable

11.ENVIRONMENTAL ISSUES

All waste is to be removed from site and disposed of in accordance with the Environmental Protection Act 1990 and Elite Services Holdings company policy.

12. FIRST AID AND EMERGENCIES

All incidents and accidents are to be reported to the customer in the first instance and then to Elite Healthcare. All ‘Elite Services Holdings’ service personnel carry 1st aid kits on their vehicles. All engineers MUST carry a mobile phone whilst working alone. In the unlikely event of an electrical accident, any form of rescue should only be done by the rescue services (999) These should be called from a safe area away from any danger and at the earliest opportunity

13. OTHER INSTRUCTIONS

Follow Safe Working Systems in order to reduce the risk of injury